## Slide 1: Optimal Energy Storage System Operation for Peak Reduction
Daisuke Kodaira, Sekyung Han
Kyungpook National University, Korea.

## Slide 2
System configuration:
・Peak shaving on distribution network (22.9kV) by network operator
・Two Energy Storage Systems (battery) are installed in the field
・ESSs are controlled by remote. The schedule is determined by the network operator 24 hours ahead
Project of peak shaving using Energy Storage System
Battery prices come down
Recover the investment

## Slide 4
Load Prediction
ESS optimization
Evaluation
The steps of peak shaving
Load Prediction
- How much is the peak tomorrow?
- When will the peak comes tomorrow?
ESS optimization
- What is the best schedule of ESSs?
Evaluation
- How much we shaved the peak?

## Slide 5
1
2
3
････
23
0
MW
6
hour
Now
Observed Load
Predicted Load
Line capacity
10
The prediction is not always reliable….
ESS cannot reduce the peak appropriately
in case the prediction has error
“Prediction tells us
we don’t need to
operate ESS for peak”
Load on feeder
Load Prediction - problem

## Slide 6
The concept of probability is necessary to evaluate the risk
“Prediction tells us
the load falls into gray zone with 95% probability”
Probabilistic Interval (PI)
Prediction with PI is proposed by many existing studies
How can we utilize the PI for ESS control?
Load Prediction - solution
Line capacity

## Slide 7
3
Probability
5
8
････
0
Load [MW]
Probability
････
Load Prediction
Load [MW]
8
11
14
5

## Slide 8
5
10
1
Probability
MW
Probability
MW
am0:00 ~ am1:00
t ~ t+1
95% PI
95% PI
4
6
Upper
boundary
Lower
boundary
ESS optimized schedule

## Slide 9
How can we build Prediction Intervals (PIs)?
Now, Let’s assume we are ESS operator. We have to select the one of the prediction algorithm and boundaries. How can we chose one of them?
My algorithm tell the boundary containing 100% data set.
But the width is wider.
My algorithm tell the boundary containing 90% data set.
The width is smaller.

## Slide 10
Various PIs example
Each PI has another boundaries. Sample base shows the most optimistic one and Chebyshev shows the most pessimistic one
Chebyshev
Confidence Interval
Sample base
Past Load and PIs

## Slide 11
Construction of PIs
Pick the 5% and 95% data in ascending data as the boundaries.
1 2 3 4 5 6 7 8 9 10
The data is assumed to follow the normal distribution, calculate 95% CI
Confidence Interval
Chebyshev
Sample base
Chebyshev’s inequality ensure the certain percentage of data lays in certain range

## Slide 12
Construction of PIs - Chebyshev
Chebyshev’s inequality
Chebyshev’s inequality ensure the certain probability as the sample lays in certain range
When extracting one sample from a certain random variable , the probability that it is greater than is or less.

## Slide 13
Error distribution and PIs
Each hour has error distribution respectively
The error is obtained by the past data prediction
・・・・・
Probability
Error rate[%]
Deterministic prediction
Deterministic prediction
Day 1
Day 2
Day 3
Error distribution
for 0am~1am
Deterministic prediction
Window
Confidence Interval
Chebyshev

## Slide 14
PI evaluation - CWC
1. How wide the boundary is?
- Normalized mean prediction interval width (NMPIW)
2. How many data falls into the boundary?
The PI coverage probability (PICP)
Ex) Nominal boundary = 90%
Actual boundary(PICP) = 89%
There are general criterion – The coverage-width-based criterion (CWC)
Smaller CWC is better score.

## Slide 15
PIs for one day prediction
(c) Chebyshev
a) Sample base
(b) confidence interval
 | Sample | CI | Chebyshev
Coverage rate | 57% | 79% | 100%
Normalized PI width | 0.25 | 0.4 | 0.79
CWC score | 3.2E+12 | 1674 | 0.78
Which PI derives the best performance on the peak reduction?
Let’s assume we predict tomorrows load with PIs

## Slide 16
ESS schedules – various PIs
a) Sample base
ESS discharges around 8am and 11pm

## Slide 17
b) confidence interval
ESS discharges around 8am and 11pm as window case
ESS schedules – various PIs

## Slide 18
c) Chebyshev
ESS discharge focuses on only around 8am
because of the highest peak around 8am
ESS schedules – various PIs

## Slide 19
Operation result for one day
Sample base and CI can reduce the peak properly, but
Chevshyev increases the peak from 6.5MW to 6.8MW
 | sample | CI | Chevshyev
Observed load [MW] | 6.5 |  | 
Adjusted Observed load [MW] | 6.0 (-7.6%) | 6.0 (-7.6%) | 6.8 (+4.6%)
Operation result with sample base PI

## Slide 20
Window PI derives the best performance through a year
even though the its CWC score is the worst among 3 methods
 | Sample | Confidence interval | Chevshyev
Median of Reduction [MW] | -0.13 | -0.09 | +0.06
Average of Reduction [MW] | -0.21 | -0.19 | +0.008
The highest peak in a year [MW] | 10.05 -> 9.88(-1.6%) | 10.05 -> 9.82(-2.2%) | 10.05 -> 9.96(-0.89%)
(c) Chebyshev
a) Sample base
(b) Confidence interval
Yearly peak reduction on each PIs
reduction
reduction
reduction
Operation result for one year

## Slide 21
 | Sample base | Confidence interval | No error prediction (ideal operation )
Median of Reduction [MW] | -0.13 | -0.09 | -0.81
Average of Reduction [MW] | -0.21 | -0.19 | -0.76
The highest peak in a year [MW] | 10.05 -> 9.88(-1.6%) | 10.05 -> 9.82(-2.2%) | 10.05 -> 8.91(-11.3%)
Operation result for one year
reduction
reduction
reduction
a) Sample base
(b) Confidence interval
(d) ideal operation
Why the highest peak is not reduced as ideal operation by the proposed PIs?

## Slide 22
Peak reduced 10.5 -> 9.03 (-1.47MW) 14% reduction (ideal reduction is 15%)
All observed data lay inside of PI
During 0:00-1:00, the prediction is underestimated but PI covers the error properly
During 7:00-9:00, load is mitigated because of the high upper CI(risk assessment)
During 23:00-24:00, peak is properly reduced
The highest peak in a year (Confidence interval case)
How does the original highest peak change by ESS operation?

## Slide 23
Peak increased 9.35 -> 9.82 (+0.47MW) 4.7% increase
During 0:00-1:00, observed data is out of the PI (Prediction error) 5% phenomenon?
During 9:00-10:00, Upper CI is large and it is mitigated (Risk assessment)
The highest peak in a year (Confidence interval case)
How is the new highest peak after ESS operation?

## Slide 24
Discussion3: Problem statement
Originally, objective function doesn’t care the off-peak duration. (That’s why PI increased by ESS operation during 0-1am)
-> What if we consider the off-peak duration too?
peak
off-peak

## Slide 25
MW
hour
Load on feeder [MW]
hour
Load on feeder [MW]
Prediction
Case1
Case2
Case3
Case1
Actual
Discussion3: Concept of new objective function

## Slide 26
5
10
1
Probability
MW
Probability
MW
am0:00 ~ am1:00
t ~ t+1
95% PI
95% PI
4
6
Upper
boundary
Lower
boundary
Discussion3: Modified objective function
; standard deviation of the upper boundaries
Notes: ・Intuitively, we want to flat the PI. The “Flat” can be realized by minimizing the standard deviation (or variance) of PI from 0-24. The blue term is new variable to flat the PIs.

## Slide 27
Discussion3: operation result vs previous Objective function
Previous objective function |  | Sample base | Confidence interval | Chevshyev | No error prediction
Median of Reduction [MW] |  | -0.13 | -0.09 | +0.06 | -0.81
Average of Reduction [MW] |  | -0.21 | -0.19 | +0.008 | -0.76
The highest peak in a year [MW] |  | 10.05 -> 9.88 (-1.6%) | 10.05 -> 9.82 (-2.2%) | 10.05 -> 9.96 (-0.89%) | 10.05 -> 8.91 (-11.3%)
Modified objective function | Deterministic Prediction | Sample | Confidence interval | Chevshyev | No error prediction
Median of Reduction [MW] | -0.43 (-7.2%) | -0.56 (-9.9%) | -0.58 (-9.9%) | -0.44 (-7.48%) | -0.81 (-12.1%)
Average of Reduction [MW] | -0.47 (-6.8%) | -0.60 (8.9%) | -0.61 (-9.1%) | -0.47 (-5.78%) | -0.76 (-11.8%)
The highest peak in a year [MW] | 10.05 ->9.97 (-0.8%) | 10.05 -> 9.54 (-5.1%) | 10.05 -> 9.42 (-6.2%) | 10.05 -> 9.79 (-2.5%) | 10.05 -> 8.91 (-11.3%)
Notes: *With modified objective function, the amount of reduction improved in terms of all perspectives (average, median and the highest peak).
*On the top of that, I proofed using PI realizes more reduction than using deterministic prediction. The PI (boundaries based on historical error) mitigates the negative affect of the prediction error to seek the optimal ESS schedule

## Slide 28
CWC vs peak reduction
There are no obvious relationship between CWC and peak reduction
What I expected

## Slide 29
CWC vs peak reduction
Chart: Smaple base
There are no obvious relationship between CWC and peak reduction
What I expected
What I expected

## Slide 30
Appendix

## Slide 31
ESS #1
ESS #2
PCS Cap : 1MW
ESS Cap : 2MWh
PCS Cap : 1MW
ESS Cap : 2MWh
Already installed
Will be install at this point
CB to ESS #1 : 5,824m
ESS #1 to ESS #2 : 9,598m
ESS #2 to end of line : 7,428m
Line Capacity is 10MW(max cap)
Network topology and parameters

## Slide 32
ESS#1
ESS#2
Amount of Power flow
How to flow form each ESS and substation
2)
1)
80
60
20
50
10
The algorithm evaluates the criticalness at 5 parts of feeder
A) Between substation and load1
B) Between load1 and ESS#1
C) Between ESS#1 and load2
D) Between load2 and ESS#2
E) Between ESS#2 and load3
A)
B)
C)
D)
E)
This power flow is a example.

## Slide 33
Input Data structure
longTermPastData: past load and predictors
forecastData: predictors for load forecasting
(The data measured immediately before will be utilized here in this project)

## Slide 34
Input Dataset
Building Index | Year | Month | Day | Hour | Quarter | P1(DayOfWeek) | P2(Holiday) | P3(Temp) | P4(Radiation)
1 | 2018 | 6 | 29 | 11 | 1 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 11 | 2 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 11 | 3 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 12 | 0 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 12 | 1 | 5 | 4 | 29 | 2
Data classification | Variable Name | Value
Time data (Time data showing the estimated period you specify) | BuildingIndex | Numbers indicates the buildings or sites where the system is deployed E.g. 1,2,…, etc.
 | Year | A 4-digit number representing the year E.g. 2017, 2018, etc.
 | Month | A double digit representing the month E.g. 01, 02, 03, 04, 05, 06, 07, 08, 9, 10, 11, 12
 | Day | A double-digit number representing the day E.g. 01, 02, …, 30, 31
 | Hour | A double-digit number representing time E.g. 0, 1, …, 22, 23, 24
 | Quarter | A one-digit number representing minutes E.g. 00 minutes -> 0, :15 minutes - > 1, :30 minutes -> 2, :45 minutes -> 3

## Slide 35
Input Dataset
Building Index | Year | Month | Day | Hour | Quarter | P1(DayOfWeek) | P2(Holiday) | P3(Temp) | P4(Radiation)
1 | 2018 | 6 | 29 | 11 | 1 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 11 | 2 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 11 | 3 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 12 | 0 | 5 | 4 | 29 | 2
1 | 2018 | 6 | 29 | 12 | 1 | 5 | 4 | 29 | 2
Data classification | Variable Name | Value
Predictors | Tempreature | The temperature measured by the sensors E.g. 20.0, 19.5,…, etc.
 | Radiation | The sun radiation measured by the sensors E.g. 2, 3, etc.
Before we get the measurement data, we prepare the past data from web.
As the sensors collect the data, the past data from web is updated to measurement data

## Slide 36
Implementation & libraries
matlab
On Windows
On Linux
Source is written by matlab on windows.
Our java libraries work on the windows environment and Linux environment.